## Design
1 Set nominal or BEP head, H0
2 Set nominal or BEP flow, Q0
3 Set the frequency (50 or 60 Hz)
4 Adjust the number of pole pairs until beta2 [calculated] is between 13 and 21 degrees |  |  |  |  | Q0 | 33
5 Set beta2 [shall] equal to beta2 [calculated] |  |  |  |  | L | 7.2888
[5 empty] | A | 12.5664
[5 empty] | Twt | 0.083298
INPUT |  | Values to enter into LVTrans
Grid frequency [Hz] | 50 | H BEP [m] | 23.4
eta | 0.942 | Q BEP [m3/s] | 33 |  | 17
H BEP or nom [m] | 23.4 | n [o/min] | 176.4706
Q BEP or nom [m3/s] | 33 | Speed number | 1.0695
Pole pairs | 17 | r1 [m] | 0.84684 | r1/r2 | 0.73
beta_2 [shal] | 20 | r2 [m] | 1.1601
|  | a1 BEP | 26.7123
beta_2 [calculated] | 20.007 | b1 BEP | 77.6468
|  | beta2 | NA
|  | Pole pairs | 17
|  | P BEP [MW] | 7.1432
|  | T BEP [kgm] | 386537.1467
If nominal values are used as input, then the output will be nominal values
If BEP values are used as input, then output will be BEP values

## Beregning
Innput
H0 [m] | 23.4 |  |  | omega_red [rad/m] | 0.86203 | D2 [m] | 2.3201
Q0 [m3/s] | 33 |  |  | Q_red | 1.5393 | cm2 [m/s] | 7.8056
n [o/min] | 176.4706 |  |  | Fartstall | 1.0695 | beta_2 [rad] | 0.34919
g [m/s2] | 9.82 |  |  | omega [rad/s] | 18.48 | beta_2 [grad] | 20.007
u1_red [-] | 0.73
u1 [m/s] | 15.6495 |  |  | cm2 [m/s] | 7.8027
c_u1_red [-] | 0.65753 |  |  | D2 [m] | 2.3205
c_u1 [m/s] | 14.096 |  |  | D1 [m] | 1.6937 | u1_red*rot(2gh) | 15.6495
beta_2 [grad] | 20 | må justeres |  | cm1 [m/s] | 7.0934 | rot(2*g*H0) | 21.4377
beta_2 [rad] | 0.34907 |  |  | B1 [m] | 0.87434 | a | 0.011499
u2 [m/s] | 21.4377 | 16.507 |  | alpha_1 [rad] | 0.46622 | b | 0.54005
eta_max | 0.942 |  |  | alpha_1 [grad] | 26.7123
u2_max [m/s] | 21.4377 |  |  | beta_1 [rad] | 1.3552
|  |  |  | beta_1 [grad] | 77.6468
Design
H0 [m] | 23.4
Q0 [m3/s] | 33
n [o/min] | 176.4706
Fartstall | 1.0695
D1 [m] | 1.6937 | 0.84684
D2 [m] | 2.3201 | 1.1601
alpha1 | 26.7123
beta1 | 77.6468
beta2 | 20.007 |  | Må ligge mellom 13 og 20 grader
Polpar | 17 |  | Må være heltall
P0 [MW] | 7.1432
T0 [kgm] | 386537.1467

## Design_Alab
1 Beregn en turbin i Alab |  |  |  | A1 | 4.8408
2 Sett inn verdiene i blått |  |  |  | c1m | 6.8253
|  |  |  | u1 | 25.8327
|  |  |  | cu1_red | 0.50703
|  |  |  | cu1 | 11.008
|  |  |  | alpha_1 | 31.8001
|  |  |  | cu2 | 14.8248
INPUT FRA ALAB |  | Verdier som skal inn i LVTrans |  | beta_1 | 24.7211
Nettfrekvens [Hz] | 50 | H0 [m] | 24 | omega | 19.635
Head | 24 | Q0 [m3/s] | 33.04
Best point flow | 33.04 | n [o/min] | 187.5
rpm | 187.5 | Fartstall | 1.134
Efficiency | 93.8 | r1 [m] | 1.3156
B1 [mm] | 585.6 | r2 [m] | 1.2598
D11 [mm] | 2024.1 | alpha1 | 31.8001
D12 [mm] | 2631.3 | beta1 | 24.7211
u11 | 0.925 | beta2 | NA
D22 [mm] | 2519.6 | Poler | 32
u22 | 1.151 | P0 [MW] | 7.3041
Speed number | 1.134 | T0 [kgm] | 371993.8128