## Slide 1
PID
Waterway/
turbine
1/TaS
nr
n
-
-
Pe
P
Ideal governor
Not practically realizable
No power control
Only speed control
Cannot run on the grid
y
e

## Slide 2
PID
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
Non-dimensional variables
y
e
Before we can do anything, the ability to add and subtract apples and oranges has to be made. This is done here by using non-dimensional variables with similar variations in value.
A non-dimensional value of zero corresponds to zero in engineering unit, and a non-dimensional value of 1 corresponds to the nominal value. Nominal values are the values producing nominal power. This is sometimes called per unit or pu, where the nominal power is the base unit.
n = N/N0
p = P/P0
y = Y/Y0
f = F/F0
and so on
One can see that n = f
y and p can be added and so on.

## Slide 3
PID
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
The functionality of the PID
y
e
A negative feedback loop with a PID will adjust the output, y, so the input, e, equals zero.
The PID itself will continuously increase y when e > 0 and decrease y when e < 0. This is done in a dynamic fashion governed by the P, Ti and Td parameters.
For the PID to do a useful ting, The input, e, and the output, y, has to be configured in a block diagram to create a dynamic and static balance when e equals zero.

## Slide 4
The grid
The Nordic grid

## Slide 5
The grid
Like a infinitely heavy cogwheel running at 50 Hz
Each turbine is too small to have an effect
Seen from each turbine, the speed, n, is constant (each single governor cannot change it, but it varies according to the grid frequency)

## Slide 6
Isolated grid grid
The turbine IS the cogwheel
The loads are smaller wheels with varying load
The turbine controls the speed , n

## Slide 7
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
Simple PI governor with power control
Adjustable parameters:
nr = speed reference (50 or 60 Hz)
pr = power setpoint (0 to 1.2 typically)
droop = 0.02 – 0.12 (typically 0.06)
How does it work? What does it do?
pr
droop
y1
-
e
y2

## Slide 8
Droop
P
F
Droop = -∆f/∆p ≈ - ∆f/∆y in pu
= -(∆F/F0)/(∆P/P0) ≈ - (∆F/F0)/(∆Y/Y0)

## Slide 9
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
Simple PI governor - droop function
pr
droop
y1
-
e
y2
PI
nr
n
-
droop
y1
-
e
An ordinary feedback loop
(nr - n) is the “setpoint”
Will adjust the output y1 until
e = (nr - n) - y1*droop = 0
NB! The value of droop is positive in these block diagrams

## Slide 10
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
Simple PI governor with power control
Island operation (isolated grid)
We want n = nr
Ordinary speed controller
pr
droop
y1
-
e
y2
Grid operation:
We want pr + n(droop) = p
We want droop = -∆f/∆p
We want to set the power, but let the droop run unaffected

## Slide 11
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
Simple PI governor isolated grid
pr
droop
y1
-
e
y2
pr = 0 (we do not want to set power on isolated grid)
y2 = y1
droop = 0.06 (typical value)
e = nr - n -y1*droop
e = 0 => n = nr - y1*droop
Full load: pe = 1 => p = 1 => y2 = 1
n = 1 - 1*0.06 = 0.994 (47 Hz)
droop = 0 => n = nr (always)
A speed controller, but only exact when droop = 0

## Slide 12
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
Simple PI governor isolated grid
pr
droop
y1
-
e
y2
pr = 0 (we do not want to set power on isolated grid)
y2 = y1
droop = 0.06 (typical value)
e = nr - n - y1*droop
e = 0 => n = nr - y1*droop
Zero load: pe = 0 => p = 0 => y2 ≈ 0.03
n = 1 - 0.03*0.06 = 0.9982 (49.91 Hz)
droop = 0 => n = nr (always)
A speed controller, but only exact when droop = 0

## Slide 13
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
Simple PI governor - On the grid
pr
droop
y1
-
e
y2
n is “unmovable” => pe must be p
y2 = y1 + pr
droop = 0.06 (typical value)
e = nr - n - y1*droop
n = nr => e = -y1*droop
e = 0 => y1 = 0
Full load: pr = 1 => y2 = 1
p = 1 => pe = 1
When n = nr then pe = pr (theoretically)

## Slide 14
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
Simple PI governor - On the grid
pr
droop
y1
-
e
y2
n is “unmovable” => pe must be p
y2 = y1 + pr
droop = 0.06 (typical value)
e = nr - n -y1*droop
n = 1.01*nr => e = -0.01 - y1*droop
e = 0 => y1 = -0.01/droop = -0.167
Full load: pr = 1 => y2 = 1 + y1 = 0.833 = p
pe = 0.833
When n ≠ nr then pe = pr + the effect of droop

## Slide 15
Practical governor - step 1
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
y
e
P
PD
Change from “serial” to “parallel” configuration
More practical for a digital governor

## Slide 16
Practical governor - step 2
Only derivate the measurement, not the setpoint
Include a low pass filter
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
y
e
P
(1+TdS)/(1+0,1TdS)

## Slide 17
Practical governor - step 3
Include droop and the ability to set power
PI
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
y2
e
P
(1+TdS)/(1+0,1TdS)
pr
droop
-
y1

## Slide 18
y/p
p
y
Wanted p
Assumed correct y
Decreased h
Increased h
Curves made at commissioning

## Slide 19
Ramp
Time
y
dy/dt = 1% per full stroke (typical)

## Slide 20
Practical governor - step 4
Include y/p curve, ramp and servo (simplify PI block).
Example showing the principle. Variations occurs in real governors
PI
pr
n
-
-
pe
p
(1+TdS)/(1+0,1TdS)
nr
droop
-
Servo
Waterway/
turbine
1/TaS
y/p
ramp
y
e

## Slide 21
Practical governor - step 5
Include integrator to remove error between pr and pe when running on the grid. Can be used on some power plants.
Example showing the principle. Variations occurs in real governors.
PI
pr
n
-
-
pe
p
(1+TdS)/(1+0,1TdS)
nr
droop
-
Servo
Waterway/
turbine
1/TaS
y/p
ramp
y
e
1/Tips
-

## Slide 22
Practical governor - step 5b
Move the derivation to parallel. Must be done for AFF analysis for instance.
Example showing the principle. Variations occurs in real governors.
PI
pr
n
-
-
pe
p
KpTdS/(1+0,1TdS)
nr
droop
-
Servo
Waterway/
turbine
1/TaS
y/p
ramp
y
e
1/Tips
-
-

## Slide 23
PI
Waterway/
turbine
1/TaS
pr
n
-
-
pe
p
Power related droop
(1+TdS)/(1+0,1TdS)
nr
-
droop
Servo
y
e
Droop = -∆f/∆p ≈ - ∆f/∆y
Using ∆p is 100% correct, using ∆y is an approximation (even in pu).
Power related droop will always cause power feedback, which is not always wanted

## Slide 24
PI
Waterway/
turbine
1/TaS
pr
n
-
-
pe
p
Power related droop
(1+TdS)/(1+0,1TdS)
nr
-
droop
Servo
y
e
n is “unmovable” => pe must be p
droop = 0.06 (typical value)
e = nr - n + (pr - pe)*droop
n = nr => e = (pr - pe)*droop
e = 0 => pr = pe
Full load: p = pe = pr = 1 => y = 1
When n = nr then pe = pr (exact)

## Slide 25
PI
Waterway/
turbine
1/TaS
pr
n
-
-
pe
p
Power related droop
(1+TdS)/(1+0,1TdS)
nr
-
droop
Servo
y
e
n is “unmovable” => pe must be p
droop = 0.06 (typical value)
e = nr - n + (pr - pe)*droop
n = 1.01*nr => e = -0.01 + (pr - pe)*droop
e = 0 => pe = pr - 0.01/droop
Full load: pr = 1
pe = 1 - 0.01/0.06 = 0.833
When n ≠ nr then pe = pr + the effect of droop

## Slide 26
PI
Waterway/
turbine
1/TaS
pr
n
-
-
pe
p
Power related droop, practical diagram
(1+TdS)/(1+0,1TdS)
nr
-
droop
Servo
y1
e
ramp
Forward feed from Pr to give faster power response.
Example showing the principle. Variations occurs in real governors.
y2

## Slide 27
PI
Waterway/
turbine
1/TaS
pr
n
-
-
pe
p
Power related droop, practical diagram
nr
-
droop
Servo
y1
e
ramp
Forward feed from Pr to give faster power response. Parallel connection of the derivative function, for AFF
Example showing the principle. Variations occurs in real governors.
y2
KpTdS/(1+0,1TdS)
-

## Slide 28
Power related vs opening related droop
Power related droop
The droop is 100% exact.
Always power feedback.
Only suitable for some power plants.
Opening related droop
The droop is an approximation and will never be 100% exact.
Can chose between power feedback and no power feedback.
Can be used on all power plants.

## Slide 29
Saturation
The integral calculations “saturates” when the output from the PID causes little or no change in the process value.
The integrator keeps integrating (adding) the error each time step
The servo will end up at max or at min.
PID
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
y’
e
slow servo
y

## Slide 30
Saturation
e = nr – n
If nr > n
then y increases until n = nr (e = 0)
If n = const (no change in n regardless of change in y) and nr > n
then e > 0 (always) and y will increase continuously
until the servo reach min or max.
This will also happen during transients if the output is constricted by ramps or slow servos. Will cause overshoot/undershoot.
PID
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
y’
e
slow servo
y

## Slide 31
Saturation – Anti Windup
(y – y’) * 1/Taw is added in front of the integration
Taw <= Ti
The saturation error, too much integration caused by (y – y’), is removed because it is subtracted before the integration.
This is called back substitution, other methods also exist.
PID
Waterway/
turbine
1/TaS
nr
n
-
-
pe
p
y’
e
slow servo
y
P
y’
e
slow servo
y
P/Ti
1/Taw
1/s
-